## Return of investment
System Size(KW) | 6
[6 empty] | Slab Consumption < 500 kWh | [5 empty] | Slab Consumption > 500 kWh | [5 empty] | Slab Consumption > 500 kWh
[6 empty] | FROM | TO | Rate | kWh consumed | Slab rate |  | FROM | TO | Rate | kWh consumed | Slab rate |  | FROM | TO | Rate | kWh consumed | Slab rate
System cost | 380432.184 |  | Daily generation(KW) | 25.9 |  | 401 | 500 | 6.3 |  | 0 |  | 1001 | 9999 | 11.55 | 575.5833 | 6647.9875 |  | 1001 | 9999 | 11.55 | 2248.4848 | 103938.45
Subsidy | 78000 |  | Annual Generation (KW) | 9453.5 |  | 201 | 400 | 4.7 | 200 | 940 |  | 801 | 1000 | 10.5 | 200 | 2100 |  | 801 | 1000 | 10.5 | 200 | 2100
Net Investment | 297679.3215 |  | Bi Monthly Generation | 1575.5833 |  | 101 | 200 | 2.35 | 100 | 235 |  | 601 | 800 | 9.45 | 200 | 1890 |  | 601 | 800 | 9.45 | 200 | 1890
[6 empty] | 0 | 100 | 0 | 100 | 0 |  | 501 | 600 | 8.4 | 100 | 840 |  | 501 | 600 | 8.4 | 100 | 840
[12 empty] | 401 | 500 | 6.3 | 100 | 630 |  | 401 | 500 | 6.3 | 100 | 630
Bi Monthly Saving (Rs) | 13517.9875 |  | Tariff Escalation(%) | 3% | [7 empty] | 101 | 400 | 4.7 | 300 | 1410 |  | 101 | 400 | 4.7 | 300 | 1410
Annual Saving | 81107.925 | [6 empty] | Expected bill Rs. = | 1175 |  |  | 0 | 100 | 0 | 100 | 0 |  | 0 | 100 | 0 | 100 | 0
Payback years | 3.6702 | 3 years | 9 months |  |  |  |  | Slab cost per kW = | 3.3375
ROI % p.a. | 27.2467 | [6 empty] | Bill cost per kW = | 2.9375
[14 empty] | Expected bill Rs. = | 13517.9875 |  |  |  |  | Bill value Rs. = | 32840
Inverter cost = | 54799.92 | [12 empty] | Slab cost per kW = | 7.2714 |  |  |  |  | kWh consumed = | 3248.4848
[14 empty] | Bill cost per kW = | 8.5797 |  |  |  |  | Avg. cost per kW = | 10.1093
IF NOT SOLAR |  |  | Daily usage(KW) | 25.9 |  |  |  |  | FROM | TO | Rate | kWh consumed | Slab rate
|  |  | Annual Usage (KW) | 9453.5 |  |  |  |  | 1001 | 9999 | 11.55 | 575.5833 | 6647.9875
|  |  | Bi Monthly Usage | 1575.5833 |  |  |  |  | 801 | 1000 | 10.5 | 200 | 2100
[9 empty] | 601 | 800 | 9.45 | 200 | 1890
[9 empty] | 501 | 600 | 8.4 | 100 | 840
|  |  | Bi Monthly Expense | 13517.9875 |  |  |  |  | 401 | 500 | 6.3 | 100 | 630
|  |  | Annual Expense | 81107.925 |  |  |  |  | 101 | 400 | 4.7 | 300 | 1410
[6 empty] | RENTAL |  |  | 0 | 100 | 0 | 100 | 0
|  |  | Payback period (years) | 3.9589 |  | 1.3066
|  |  | (years, months) | 3 years | 12 months | 1 years | 4 months
|  |  |  | Tarif increase = | 2%
|  |  | Years | Yearly Bill without solar (with tarif increase) | Yearly Bill with solar | Bi-monthyl bill without solar | Bi-monthyl bill with solar | Yearly savings | Costs without solar (accumulated) | Cost of going solar (accumulated) | Break Even | Yearly savings (Rental) | Break Even (Rental) |  | Rs. per unit (for tenant) = |  | 8
|  |  | 1 | 81107.925 | 8110.7925 | 13517.9875 | 1351.7987 | 72997.1325 | 81107.925 | 305790.114 | -224682.189 | #DIV/0! | -69806.074 |  | Units consumed (yearly) = |  | 19486.53
|  |  | 2 | 82730.0835 | 8273.0084 | 13788.3473 | 1378.8347 | 74457.0752 | 163838.0085 | 314063.1224 | -150225.1139 | #DIV/0! | 157904.9577 |  | Estimated bill for tenant (yearly) = |  | 155892.24
|  |  | 3 | 84384.6852 | 8438.4685 | 14064.1142 | 1406.4114 | 75946.2167 | 248222.6937 | 322501.5909 | -74278.8972 | #DIV/0! | 305358.7291 |  | Estimated bill for renter (yearly) = |  | 8110.7925
|  |  | 4 | 86072.3789 | 8607.2379 | 14345.3965 | 1434.5396 | 77465.141 | 334295.0725 | 331108.8288 | 3186.2438 | #DIV/0! | #REF!
|  |  | 5 | 87793.8264 | 8779.3826 | 14632.3044 | 1463.2304 | 79014.4438 | 422088.899 | 339888.2114 | 82200.6876 | #DIV/0! | #REF!
|  |  | 6 | 89549.703 | 8954.9703 | 14924.9505 | 1492.495 | 80594.7327 | 511638.602 | 348843.1817 | 162795.4203 | #DIV/0! | #REF!
|  |  | 7 | 91340.697 | 9134.0697 | 15223.4495 | 1522.345 | 82206.6273 | 602979.299 | 357977.2514 | 245002.0476 | #DIV/0! | #REF!
|  |  | 8 | 93167.511 | 9316.7511 | 15527.9185 | 1552.7919 | 83850.7599 | 696146.81 | 367294.0025 | 328852.8075 | #DIV/0! | #REF!
|  |  | 9 | 95030.8612 | 9503.0861 | 15838.4769 | 1583.8477 | 85527.7751 | 791177.6712 | 376797.0886 | 414380.5826 | #DIV/0! | #REF!
|  |  | 10 | 96931.4784 | 9693.1478 | 16155.2464 | 1615.5246 | 87238.3306 | 888109.1496 | 386490.2365 | 501618.9132 | #DIV/0! | #REF!
|  |  | 11 | 98870.108 | 9887.0108 | 16478.3513 | 1647.8351 | 88983.0972 | 986979.2576 | 451177.1673 | 535802.0903 | #DIV/0! | #REF!
|  |  | 12 | 100847.5102 | 10084.751 | 16807.9184 | 1680.7918 | 90762.7591 | 1087826.768 | 461261.9183 | 626564.8495 | #DIV/0! | #REF!
|  |  | 13 | 102864.4604 | 11315.0906 | 17144.0767 | 1885.8484 | 91549.3697 | 1190691.228 | 472577.0089 | 718114.2192 | #DIV/0! | #REF!
|  |  | 14 | 104921.7496 | 12590.61 | 17486.9583 | 2098.435 | 92331.1396 | 1295612.978 | 485167.6189 | 810445.3588 | #DIV/0! | #REF!
|  |  | 15 | 107020.1846 | 13912.624 | 17836.6974 | 2318.7707 | 93107.5606 | 1402633.162 | 499080.2429 | 903552.9194 | #DIV/0! | #REF!
|  |  | 16 | 109160.5882 | 15282.4824 | 18193.4314 | 2547.0804 | 93878.1059 | 1511793.75 | 514362.7252 | 997431.0253 | #DIV/0! | #REF!
|  |  | 17 | 111343.8 | 16701.57 | 18557.3 | 2783.595 | 94642.23 | 1623137.55 | 531064.2952 | 1092073.255 | #DIV/0! | #REF!
|  |  | 18 | 113570.676 | 18171.3082 | 18928.446 | 3028.5514 | 95399.3678 | 1736708.226 | 549235.6034 | 1187472.623 | #DIV/0! | #REF!
|  |  | 19 | 115842.0895 | 19693.1552 | 19307.0149 | 3282.1925 | 96148.9343 | 1852550.316 | 568928.7586 | 1283621.557 | #DIV/0! | #REF!
|  |  | 20 | 118158.9313 | 21268.6076 | 19693.1552 | 3544.7679 | 96890.3237 | 1970709.247 | 590197.3662 | 1380511.881 | #DIV/0! | #REF!
|  |  | Total | 1970709.247 | 146601.0014 |  |  | 1732991.123 | 100% | 29.95%
| Investment savings & Breakeven year | [5 empty] | Cumulative Cost of NOT GOING vs GOING SOLAR
Bi-monthly bill of GOING SOLAR vs NOT

## Quotation
| System size = | 6000
| Items |  | Total unit | UoM | Price per unit | BoM Cost | Margin | Basic Cost | GST % | Final Cost |  | Cost per panel | Difference
Adani | Panels TOPCon DCR | 615 | 11 | nos | 26 | 175890 | 35178 | 211068 | 5% | 221621.4 | 58.26% | 20147.4 | 7522.9875
Renesys | Panels TOPCon non-DCR | 615 | 11 | nos | 17 | 115005 | 17250.75 | 132255.75 | 5% | 138868.5375 | 46.65% | 12624.4125
Deye | Inverter (On-Grid) | 12kW (3 ph) | 1 | nos | 43492 | 43492 | 8698.4 | 52190.4 | 5% | 54799.92 | 14.4%
| DCDB |  | 1 | nos | 4950 | 4950 | 990 | 5940 | 18% | 7009.2 | 1.842%
| ACDB |  | 1 | nos | 4250 | 4250 | 850 | 5100 | 18% | 6018 | 1.582%
| Mounting structure |  | LS | LS | 4000 | 24000 | 4800 | 28800 | 18% | 33984 | 8.933%
| Earthing rod | 2m, dia? | 3 | nos | 3500 | 3500 | 700 | 4200 | 18% | 4956 | 1.303%
| Lightning arrestor | 1m, dia? | 1 | nos |  | 0 | 0 | 0 | 18% | 0 | 0%
| MC4 connectors |  | 12 | nos | 42 | 504 | 100.8 | 604.8 | 18% | 713.664 | 0.1876%
| Pins & other accessories |  | LS | LS |  | 4000 | 1000 | 5000 | 18% | 5900 | 1.551%
| Design / Installation / Logistics |  | LS | LS | 3000 | 18000 | 4500 | 22500 | 18% | 26550 | 6.979%
360watts | IoT hub for energy automation |  | 1 | nos | 5000 | 5000 | 5000 | 10000 | 18% | 11800 | 3.102%
| Wiring |  |  |  | 5000 | 5000 | 1000 | 6000 | 18% | 7080 | 1.861%
[10 empty] | 380432.184 | 63.405364 / kW)
| Subsidy PM Surya Ghar |  | 6 |  | 30000 | 288586 | 62817.2 |  | 20.77% | 302432.184 | 50.405364 / kW) |  | DCR
[6 empty] | 227701 | 43889.95 |  | 14.74% | 297679.3215 | 49.61322025 / kW) |  | non-DCR | Rs. 44652
| ADDITIONAL COST: |  | meter | cost | wiring total cost |  |  |  |  | 4752.8625 | Difference
| DC cable (Panels to DCDB/Inverter) | 6 sq. mm
| AC cable (Inverter to ACDB) | 6 sq. mm 4-core
| AC cable | 4 sq mm |  | ~60/m
| Earthing cable | DC (6 sq. mm) |  | ~66/m
|  | DC (10 sq. mm) |  | ~139/m
|  | AC (6 sq. mm) |  | ~100/m
|  | AC (10 sq. mm) |  | ~150/m
TOTAL
QUOTATION
MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ PH: 9087610051
2456.7797
| To |  |  |  | 14.03.2026
Shakthi Electricals
Avinashi
| Items | Details | Basic Cost | GST % | Final Cost
| Panels (Adani TOPCon / 9 panels) | 615Wp | 142065 | 5% | 149168.25
| Inverter (1-ph On-Grid) | 5kW (1P) | 32830 | 5% | 34471.5
| DCDB | 1 nos | 5750 | 18% | 6785
| ACDB | 1 nos | 12650 | 18% | 14927
| Mounting structure (GI) | LS | 29610 | 18% | 34939.8
| Earthing rod | 3 nos | 2760 | 18% | 3256.8
| Lightning arrestor | 1 nos | 1610 | 18% | 1899.8
| MC4 connectors | 6 nos | 345 | 18% | 407.1
| Pins & other accessories | LS | 2817.5 | 18% | 3324.65
| Design & Installation |  | 30000 | 18% | 35400
|  |  | TOTAL PRICE (incl. GST) |  | 284579.9
ADDITIONAL COST (to be assessed after site visit) :
DC cable
Earthing cable
4sq mm AC cable
CUSTOMER SCOPE:
Electrical works
Civil works
TANGEDCO fee
| QUOTATION | [11 empty] | QUOTATION |  |  |  |  | QUOTATION
|  | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051 | [11 empty] | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051 |  |  |  |  | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051
| To |  |  |  | 14.03.2026 | [7 empty] | To |  |  |  | 23.03.2026 | To |  |  |  | 23.03.2026
| Shakthi Electricals | [11 empty] | Shakthi Electricals |  |  |  |  | Shakthi Electricals
| Avinashi | [11 empty] | Avinashi |  |  |  |  | Avinashi
| Items | Details | Basic Cost | GST % | Final Cost | [7 empty] | Items | Details | Basic Cost | GST % | Final Cost | Items | Details | Basic Cost | GST % | Final Cost
| Panels (TOPCon / 16 panels) | 615Wp | 227304 | 5% | 238669.2 | [7 empty] | Panels (TOPCon / 3 panels) | 615Wp | 45460.8 | 5% | 47733.84 | Panels (TOPCon / 4 panels) | 615Wp | 56826 | 5% | 59667.3
| Inverter (3-ph On-Grid) | 10kW | 63393.4 | 5% | 66563.07 | [7 empty] | Inverter (On-Grid) | 2kW | 12678.68 | 5% | 13312.614 | Inverter (On-Grid) | 2kW | 12678.68 | 5% | 13312.614
| DCDB | 1 nos | 10075 | 18% | 11888.5 | [7 empty] | DCDB | 1 nos | 2015 | 18% | 2377.7 | DCDB | 1 nos | 2015 | 18% | 2377.7
| ACDB | 1 nos | 5525 | 18% | 6519.5 | [7 empty] | ACDB | 1 nos | 1105 | 18% | 1303.9 | ACDB | 1 nos | 1105 | 18% | 1303.9
| Mounting structure (GI) | LS | 105000 | 18% | 123900 | [7 empty] | Mounting structure (GI) | LS | 18471.6102 | 18% | 21796.5 | Mounting structure (GI) | LS | 21000 | 18% | 24780
| Earthing rod | 7 nos | 6720 | 18% | 7929.6 | [7 empty] | Earthing rod | 2 nos | 1344 | 18% | 1585.92 | Earthing rod | 2 nos | 1344 | 18% | 1585.92
| Lightning arrestor | 3 nos | 5880 | 18% | 6938.4 | [7 empty] | Lightning arrestor | 1 nos | 1176 | 18% | 1387.68 | Lightning arrestor | 1 nos | 1176 | 18% | 1387.68
| MC4 connectors | 14 nos | 900 | 18% | 1062 | [7 empty] | MC4 connectors | 3 nos | 180 | 18% | 212.4 | MC4 connectors | 4 nos | 180 | 18% | 212.4
| Pins & other accessories | LS | 8400 | 18% | 9912 | [7 empty] | Pins & other accessories | LS | 1680 | 18% | 1982.4 | Pins & other accessories | LS | 1680 | 18% | 1982.4
| Design & Installation | LS | 65000 | 18% | 76700 | [7 empty] | Design & Installation | LS | 13000 | 18% | 15340 | Design & Installation | LS | 13000 | 18% | 15340
| TOTAL PRICE (incl. GST) |  |  |  | 550082.27 | [7 empty] | TOTAL PRICE (incl. GST) |  |  |  | 107032.954 | TOTAL PRICE (incl. GST) |  |  |  | 121949.914
| ADDITIONAL COST (to be assessed after site visit) : | [11 empty] | ADDITIONAL COST (to be assessed after site visit) : |  |  |  |  | ADDITIONAL COST (to be assessed after site visit) :
| DC cable | [11 empty] | DC cable |  |  |  |  | DC cable
| Earthing cable | [11 empty] | Earthing cable |  |  |  |  | Earthing cable
| 4sq mm AC cable | [11 empty] | 4sq mm AC cable |  |  |  |  | 4sq mm AC cable
| CUSTOMER SCOPE: | [11 empty] | CUSTOMER SCOPE: |  |  |  |  | CUSTOMER SCOPE:
| Electrical works | [11 empty] | Electrical works |  |  |  |  | Electrical works
| Civil works | [11 empty] | Civil works |  |  |  |  | Civil works
| TANGEDCO fee | [11 empty] | TANGEDCO fee |  |  |  |  | TANGEDCO fee
QUOTATION
MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051
| To |  |  |  | 08.04.2026
Avinashi
| Items | Details | Basic Cost | GST % | Final Cost
| Panels (Warree TOPCon) | 700 | 196000 | 5% | 205800 | 16 panels
| Panels (Adani TOPCon) | 625 | 202500 | 5% | 212625 | 18 panels
| Inverter (Deye 1-ph On-Grid) | 10kW (1 ph) | 45281 | 5% | 47545.05
| DCDB | 1 nos | 7750 | 18% | 9145
| ACDB | 1 nos | 4250 | 18% | 5015
| Earthing rod | 3 nos | 2457 | 18% | 2899.26
| Lightning arrestor | 1 nos |  | 18%
| MC4 connectors | 15 nos | 630 |  | 743.4
| Mounting structure | LS |  | 18% | 60k+
| Pins & other accessories | LS
Design / Installation / Logistics
| TOTAL PRICE (incl. GST) |  |  |  | 271147.71
ADDITIONAL COST (to be assessed after site visit) :
| DC cable (Panels to DCDB/Inverter) | 6 sq. mm
| AC cable (Inverter to ACDB) | 6 sq. mm 4-core
| AC cable | 4 sq mm
| Earthing cable | DC (6 sq. mm) | ~66/m
|  | DC (10 sq. mm) | ~139/m
|  | AC (6 sq. mm) | ~100/m
|  | AC (10 sq. mm) | ~150/m
CUSTOMER SCOPE:
Electrical works
Civil works
TANGEDCO fee

## On-grid System sizing calculato
[5 empty] | EB | SOLAR |  |  |  | To bill Rs. / kWh = | 8
Irradiance | Months | (2025-2026) kWh | (2025-2026) Bill | 2024-2025 | Avg Rs. /kWh | Daily kWh | 2m kWh | net import | Avg Rs. /kWh | To bill | Savings | Parameters | Normal System | Future expansion | EV alone | units
| May | 3377.53 | 29650.47 |  |  |  | 3240 | 21708 | 2.024 | 0 | -6557.7485 | Daily Consumption (AC) | 8.5 | 8 | 17.3571 | kWh
| April |  |  | 749.11 | [7 empty] | Energy Needed (AC) | 8.5 | 8 | 17.3571 | kWh
| March | 3069.29 | 26090.3 |  | 8.5004 | 54 | 2880 | 19296 | 2.277 | 0 | -6557.7485 | Desired AC output (from inverter) | 1.8889 | 1.7778 | 3.8571 | kW
| February |  |  | 416.2 | [7 empty] | Power Factor (PF) | 1 | 1 | 1
| January | 2340.71 | 17798.8 |  | 7.604 | 48 | 2880 | 19296 | 2.277 | 0 | -6557.7485 | Required AC output (from inverter) | 1.8889 | 1.7778 | 3.8571 | kVA | Reactive power (kVA) (i.e. useful energy) = Desired AC output / PF
| December |  |  | 399 | [7 empty] | Corresponding DC sizing | 2.0778 | 2.2222 | 4.8214 | kW | DC/AC ratio = 1.25
| November | 5336 | 52389.45 |  | 9.8181 | 48 | 2880 | 495.8 | 2.277 | 22448 | 15890.2515
| October | 2806 | 20392.05 | 415.02 | 7.2673
| September |  |  |  |  | 48 | 2880 | 19296 | 2.277 | 0 | -6557.7485
| August |  |  | 405.58
| July |  |  |  |  | 48 | 0 | 0 | #DIV/0! | 0 | #DIV/0! | Panels Age(Years) | Expected Output N.S (KWh) | Expected Output with EV (KWh)
| June |  |  | 705.4 | [7 empty] | 10 | 1.7965 | 3.6686
| May | 2557 | 20218.5 | [8 empty] | 15 | 1.7521 | 3.5778
|  | 19486.53 | 166539.57 | 3090.31 |  |  | 14760 | 80091.8 | #DIV/0! | 22448 | #DIV/0! | 20 | 1.7087 | 3.4892
| Daily consumption (kWh) = | 53.3878 | Rs. 8.55 | 8.4666 | 8.2975 | 49.2
| QUESTIONS: 1. Do you install new AC in the Mar/Apr 2025? --> due to observed additional 300-600 units bi-monthly since last 6 bills |  |  | FUTURE PLANS: 1. Plans to purchase EV car in next 12 to 24 months? 2. New appliances in next 12 months? Eg. Dishwasher, AC, etc.
[13 empty] | w/o EV |  | with EV
[12 empty] | Panel Wp | 620 | 610 | 615
[12 empty] | No of panels | 3 | 7 | 11
[12 empty] | Available inverter size (kW) | 12 | 8 | 6
[12 empty] | Actual DC sizing (kW) | 1.86 | 4.27 | 6.765
| Data needed | Column 1 |  | Months | Energy usage (units) |  | Months | Energy usage (units) |  |  |  | Actual DC/AC ratio | 0.155 | 0.53375 | 1.1773
| Average peak sun hour | 4.5 |  | EV Brand name | TATA Nexon |  | EV Brand name
| Total system losses (%) | 25 |  | Battery Capacity | 45 |  | Battery Capacity Battery Capacity | 0
| Derate factor (%) | 0 |  | Full charging times per week | 3 |  | Full charging times per week | 4
| Performance ratio | 1 |  | Extra power needed(KWh) per day | 17.3571 |  | Extra power needed(KWh) per day | 0

## Commercial RoI
System Size(KW) | 25
[6 empty] | Slab Consumption < 500 kWh | [5 empty] | Slab Consumption > 500 kWh | [5 empty] | Slab Consumption > 500 kWh
[6 empty] | FROM | TO | Rate | kWh consumed | Slab rate |  | FROM | TO | Rate | kWh consumed | Slab rate |  | FROM | TO | Rate | kWh consumed | Slab rate
System cost | 2100000 |  | Daily generation(KW) | 80 |  | 401 | 500 | 6.3 |  | 0 |  | 1001 | 9999 | 11.55 | 3866.6667 | 44660 |  | 1001 | 9999 | 11.55 | 3754.5455 | 103938.45
Fixed cost |  |  | Annual Generation (KW) | 29200 |  | 201 | 400 | 4.7 |  | 0 |  | 801 | 1000 | 10.5 | 200 | 2100 |  | 801 | 1000 | 10.5 | 200 | 2100
Net Investment | 2100000 |  | Bi Monthly Generation | 4866.6667 |  | 101 | 200 | 2.35 |  | 0 |  | 601 | 800 | 9.45 | 200 | 1890 |  | 601 | 800 | 9.45 | 200 | 1890
[6 empty] | 0 | 100 | 0 |  | 0 |  | 501 | 600 | 8.4 | 100 | 840 |  | 501 | 600 | 8.4 | 100 | 840
[12 empty] | 401 | 500 | 6.3 | 100 | 630 |  | 401 | 500 | 6.3 | 100 | 630
Bi Monthly Saving (Rs) | 51530 |  | Tariff Escalation(%) | 3% | [7 empty] | 101 | 400 | 4.7 | 300 | 1410 |  | 201 | 400 | 4.7 | 200 | 940
Annual Saving | 309180 | [6 empty] | Expected bill Rs. = | 0 |  |  | 0 | 100 | 0 | 100 | 0 |  | 101 | 200 | 2.35 | 100 | 235
Payback years | 6.7922 | 6 years | 10 months |  |  |  |  | Slab cost per kW = | 3.3375 | [8 empty] | 0 | 100 | 0 | 100 | 0
ROI % p.a. | 14.7229 | [6 empty] | Bill cost per kW = | #DIV/0!
[14 empty] | Expected bill Rs. = | 51530 |  |  |  |  | Bill value Rs. = | 50000
Inverter cost = | 54799.92 | [12 empty] | Slab cost per kW = | 7.2714 |  |  |  |  | kWh consumed = | 4754.5455
[14 empty] | Bill cost per kW = | 10.5884 |  |  |  |  | Avg. cost per kW = | 10.5163
IF NOT SOLAR |  |  | Daily usage(KW) | 8 |  |  |  |  | FROM | TO | Rate | kWh consumed | Slab rate
|  |  | Annual Usage (KW) | 2920 |  |  |  |  | 1001 | 9999 | 11.55 | 0 | 0
|  |  | Bi Monthly Usage | 486.6667 |  |  |  |  | 801 | 1000 | 10.5 | 0 | 0
[9 empty] | 601 | 800 | 9.45 | 0 | 0
[9 empty] | 501 | 600 | 8.4 | 0 | 0
|  |  | Bi Monthly Expense | 1732.85 |  |  |  |  | 401 | 500 | 6.3 | 89.6667 | 564.9
|  |  | Annual Expense | 10397.1 |  |  |  |  | 201 | 400 | 4.7 | 199 | 935.3
[6 empty] | RENTAL |  |  | 101 | 200 | 2.35 | 99 | 232.65
|  |  | Payback period (years) | #N/A |  | #N/A |  |  | 0 | 100 | 0 | 99 | 0
|  |  | (years, months) | #N/A | #N/A | #N/A | #N/A
|  |  |  | Tarif increase = | 3%
|  |  | Years | Yearly Bill without solar (with tarif increase) | Yearly Bill with solar | Bi-monthyl bill without solar | Bi-monthyl bill with solar | Yearly savings | Costs without solar (accumulated) | Cost of going solar (accumulated) | Break Even | Yearly savings (Rental) | Break Even (Rental) |  | Rs. per unit (for tenant) = |  | 8
|  |  | 1 | 10397.1 | 1039.71 | 1732.85 | 173.285 | 9357.39 | 10397.1 | 2101039.71 | -2090642.61 | #DIV/0! | -1865055.67 |  | Units consumed (yearly) = |  | 19486.53
|  |  | 2 | 10709.013 | 1070.9013 | 1784.8355 | 178.4836 | 9638.1117 | 21106.113 | 2102110.611 | -2081004.498 | #DIV/0! | -1630142.531 |  | Estimated bill for tenant (yearly) = |  | 155892.24
|  |  | 3 | 11030.2834 | 1103.0283 | 1838.3806 | 183.8381 | 9927.2551 | 32136.3964 | 2103213.64 | -2071077.243 | #DIV/0! | -1475353.32 |  | Estimated bill for renter (yearly) = |  | 1039.71
|  |  | 4 | 11361.1919 | 1136.1192 | 1893.532 | 189.3532 | 10225.0727 | 43497.5883 | 2104349.759 | -2060852.171 | #DIV/0! | #REF!
|  |  | 5 | 11702.0276 | 1170.2028 | 1950.3379 | 195.0338 | 10531.8249 | 55199.6159 | 2105519.962 | -2050320.346 | #DIV/0! | #REF!
|  |  | 6 | 12053.0885 | 1205.3088 | 2008.8481 | 200.8848 | 10847.7796 | 67252.7044 | 2106725.27 | -2039472.566 | #DIV/0! | #REF!
|  |  | 7 | 12414.6811 | 1241.4681 | 2069.1135 | 206.9114 | 11173.213 | 79667.3855 | 2107966.739 | -2028299.353 | #DIV/0! | #REF!
|  |  | 8 | 12787.1216 | 1278.7122 | 2131.1869 | 213.1187 | 11508.4094 | 92454.5071 | 2109245.451 | -2016790.944 | #DIV/0! | #REF!
|  |  | 9 | 13170.7352 | 1317.0735 | 2195.1225 | 219.5123 | 11853.6617 | 105625.2423 | 2110562.524 | -2004937.282 | #DIV/0! | #REF!
|  |  | 10 | 13565.8573 | 1356.5857 | 2260.9762 | 226.0976 | 12209.2715 | 119191.0996 | 2111919.11 | -1992728.01 | #DIV/0! | #REF!
|  |  | 11 | 13972.833 | 1397.2833 | 2328.8055 | 232.8805 | 12575.5497 | 133163.9326 | 2168116.313 | -2034952.381 | #DIV/0! | #REF!
|  |  | 12 | 14392.018 | 1439.2018 | 2398.6697 | 239.867 | 12952.8162 | 147555.9506 | 2169555.515 | -2021999.565 | #DIV/0! | #REF!
|  |  | 13 | 14823.7785 | 1482.3779 | 2470.6298 | 247.063 | 13341.4007 | 162379.7291 | 2171037.893 | -2008658.164 | #DIV/0! | #REF!
|  |  | 14 | 15268.4919 | 1526.8492 | 2544.7486 | 254.4749 | 13741.6427 | 177648.2209 | 2172564.742 | -1994916.521 | #DIV/0! | #REF!
|  |  | 15 | 15726.5466 | 1572.6547 | 2621.0911 | 262.1091 | 14153.892 | 193374.7676 | 2174137.397 | -1980762.629 | #DIV/0! | #REF!
|  |  | 16 | 16198.343 | 1619.8343 | 2699.7238 | 269.9724 | 14578.5087 | 209573.1106 | 2175757.231 | -1966184.12 | #DIV/0! | #REF!
|  |  | 17 | 16684.2933 | 1668.4293 | 2780.7156 | 278.0716 | 15015.864 | 226257.4039 | 2177425.66 | -1951168.256 | #DIV/0! | #REF!
|  |  | 18 | 17184.8221 | 1718.4822 | 2864.137 | 286.4137 | 15466.3399 | 243442.226 | 2179144.143 | -1935701.917 | #DIV/0! | #REF!
|  |  | 19 | 17700.3668 | 1770.0367 | 2950.0611 | 295.0061 | 15930.3301 | 261142.5928 | 2180914.179 | -1919771.586 | #DIV/0! | #REF!
|  |  | 20 | 18231.3778 | 1823.1378 | 3038.563 | 303.8563 | 16408.24 | 279373.9706 | 2182737.317 | -1903363.346 | #DIV/0! | #REF!
|  |  | Total | 279373.9706 | 19337.4768 |  |  | 251436.5735 | 100% | 781.3%
| Investment savings & Breakeven year | [5 empty] | Cumulative Cost of NOT GOING vs GOING SOLAR
Bi-monthly bill of GOING SOLAR vs NOT

## Commercial Quotation
| System size = | 25000 | [13 empty] | System size = | 15000
| Items |  | Total unit | UoM | Price per unit | BoM Cost | Margin | Basic Cost | GST % | Final Cost | [5 empty] | Items |  | Total unit | UoM | Price per unit | BoM Cost | Margin | Basic Cost | GST % | Final Cost
Waaree | Panels TOPCon non-DCR (20kW) | 560 | 42 | nos | 16 | 376320 | 75264 | 451584 | 5% | 474163.2 | 31.66% |  |  |  | Waaree | Panels TOPCon non-DCR (20kW) | 560 | 30 | nos | 16.5 | 277200 | 55440 | 332640 | 5% | 349272 | 16.56%
Solis | Inverter (On-Grid) | 25kW (3 ph) | 1 | nos | 69766 | 69766 | 13953.2 | 83719.2 | 5% | 87905.16 | 5.87% |  |  |  | Solis | Inverter (On-Grid) | 25kW (3 ph) | 1 | nos | 69766 | 69766 | 20929.8 | 90695.8 | 5% | 95230.59 | 6.359%
Deye | Inverter (Hybrid) | 20kW (3 ph) | 1 | nos | 265846 | 265846 | 53169.2 | 319015.2 | 5% | 334965.96 | 22.37% |  |  |  | Deye | Inverter (Hybrid) | 20kW (3 ph) | 1 | nos | 204488 | 204488 | 61346.4 | 265834.4 | 5% | 279126.12 | 18.64%
Deye | BESS | 16kWh | 1 | nos | 203597 | 203597 | 40719.4 | 244316.4 | 18% | 288293.352 | 19.25% |  |  |  | Deye | BESS | 100kWh | 4 | nos | 200391 | 801564 | 160312.8 | 961876.8 | 18% | 1135014.624 | 75.79%
Festa Solar | DCDB |  | 1 | nos | 10200 | 10200 | 3060 | 13260 | 18% | 15646.8 | 1.045% |  |  |  | Festa Solar | DCDB |  | 1 | nos | 10200 | 10200 | 3060 | 13260 | 18% | 15646.8 | 1.045%
Festa Solar | ACDB |  | 1 | nos | 4500 | 4500 | 1350 | 5850 | 18% | 6903 | 0.4609% |  |  |  | Festa Solar | ACDB |  | 1 | nos | 14300 | 14300 | 4290 | 18590 | 18% | 21936.2 | 1.465%
| Battery box |  | 1 |  | 10000 | 10000 | 3000 | 13000 | 18% | 15340 | 1.024% |  |  |  |  | Battery box |  | 1 |  | 7700 | 7700 | 2310 | 10010 | 18% | 11811.8 | 0.7887%
| Mounting structure |  | LS | LS | 4000 | 100000 | 25000 | 125000 | 18% | 147500 | 9.849% |  |  |  |  | Mounting structure |  | LS | LS | 4000 | 60000 | 15000 | 75000 | 18% | 88500 | 5.909%
| Earthing rod | 2m, dia? | 3 | nos | 2457 | 2457 | 491.4 | 2948.4 | 18% | 3479.112 | 0.2323% |  |  |  |  | Earthing rod | 2m, dia? | 3 | nos | 2457 | 2457 | 491.4 | 2948.4 | 18% | 3479.112 | 0.2323%
| Lightning arrestor | 1m, dia? | 1 | nos |  | 0 | 0 | 0 | 18% | 0 | 0% |  |  |  |  | Lightning arrestor | 1m, dia? | 1 | nos |  | 0 | 0 | 0 | 18% | 0 | 0%
| MC4 connectors |  | 41 | nos | 42 | 1722 | 344.4 | 2066.4 | 18% | 2438.352 | 0.1628% |  |  |  |  | MC4 connectors |  | 33 | nos | 42 | 1386 | 277.2 | 1663.2 | 18% | 1962.576 | 0.131%
| Pins & other accessories |  | LS | LS |  | 5000 | 2000 | 7000 | 18% | 8260 | 0.5516% |  |  |  |  | Pins & other accessories |  | LS | LS |  | 5000 | 2000 | 7000 | 18% | 8260 | 0.5516%
| Design / Installation / Logistics |  | LS | LS | 4000 | 100000 | 20000 | 120000 | 18% | 141600 | 9.455% |  |  |  |  | Design / Installation / Logistics |  | LS | LS | 5000 | 75000 | 15000 | 90000 | 18% | 106200 | 7.091%
360watts | IoT hub for energy automation |  | 1 | nos | 0 | 0 | 0 | 0 | 18% | 0 | 0% |  |  |  | 360watts | IoT hub for energy automation |  | 1 | nos | 25000 | 25000 | 0 | 25000 | 18% | 29500 | 1.97%
| Wiring |  |  |  | 50000 | 50000 | 0 | 50000 | 18% | 59000 | 3.94% |  |  |  |  | Wiring |  |  |  | 50000 | 50000 | 0 | 50000 | 18% | 59000 | 3.94%
[6 empty] | 1129642 | 224398.4 | 1437759.6 |  | 1497589.776 | 14.98% | 59.90359104 / kW) | HYBRID | 3.9736 | [6 empty] | 1534295 | 319527.8 | 1944518.6 |  | 2109709.232 | 15.15% | 140.647282133333 / kW) | HYBRID | 7.4399
| ADDITIONAL COST: |  |  |  |  | 719965 | 141463 |  |  | 946895.624 | 14.94% | 37.87582496 / kW) | ON-GRID | 3.4787 |  | ADDITIONAL COST: | [5 empty] | 116488.4 |  |  | 778987.278 | 14.95% | 51.9324852 / kW) | ON-GRID | 22.3198
| DC cable (Panels to DCDB/Inverter) | 6 sq. mm
| AC cable (Inverter to ACDB) | 6 sq. mm 4-core
| AC cable | 4 sq mm
| Earthing cable | DC (6 sq. mm) |  | ~66/m
|  | DC (10 sq. mm) |  | ~139/m
|  | AC (6 sq. mm) |  | ~100/m
|  | AC (10 sq. mm) |  | ~150/m
QUOTATION
MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ PH: 9087610051
2456.7797
| To |  |  |  | 14.03.2026
Shakthi Electricals
Avinashi
| Items | Details | Basic Cost | GST % | Final Cost
| Panels (Adani TOPCon / 9 panels) | 615Wp | 142065 | 5% | 149168.25
| Inverter (1-ph On-Grid) | 5kW (1P) | 32830 | 5% | 34471.5
| DCDB | 1 nos | 5750 | 18% | 6785
| ACDB | 1 nos | 12650 | 18% | 14927
| Mounting structure (GI) | LS | 29610 | 18% | 34939.8
| Earthing rod | 3 nos | 2760 | 18% | 3256.8
| Lightning arrestor | 1 nos | 1610 | 18% | 1899.8
| MC4 connectors | 6 nos | 345 | 18% | 407.1
| Pins & other accessories | LS | 2817.5 | 18% | 3324.65
| Design & Installation |  | 30000 | 18% | 35400
|  |  | TOTAL PRICE (incl. GST) |  | 284579.9
ADDITIONAL COST (to be assessed after site visit) :
DC cable
Earthing cable
4sq mm AC cable
CUSTOMER SCOPE:
Electrical works
Civil works
TANGEDCO fee
| QUOTATION | [11 empty] | QUOTATION |  |  |  |  | QUOTATION
|  | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051 | [11 empty] | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051 |  |  |  |  | MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051
| To |  |  |  | 14.03.2026 | [7 empty] | To |  |  | 23.03.2026 |  | To |  |  |  | 23.03.2026
| Shakthi Electricals | [11 empty] | Shakthi Electricals |  |  |  |  | Shakthi Electricals
| Avinashi | [11 empty] | Avinashi |  |  |  |  | Avinashi
| Items | Details | Basic Cost | GST % | Final Cost | [7 empty] | Items | Details | GST % | Final Cost |  | Items | Details | Basic Cost | GST % | Final Cost
| Panels (TOPCon / 16 panels) | 615Wp | 227304 | 5% | 238669.2 | [7 empty] | Panels (TOPCon / 3 panels) | 615Wp | 5% | 47733.84 |  | Panels (TOPCon / 4 panels) | 615Wp | 56826 | 5% | 59667.3
| Inverter (3-ph On-Grid) | 10kW | 63393.4 | 5% | 66563.07 | [7 empty] | Inverter (On-Grid) | 2kW | 5% | 13312.614 |  | Inverter (On-Grid) | 2kW | 12678.68 | 5% | 13312.614
| DCDB | 1 nos | 10075 | 18% | 11888.5 | [7 empty] | DCDB | 1 nos | 18% | 2377.7 |  | DCDB | 1 nos | 2015 | 18% | 2377.7
| ACDB | 1 nos | 5525 | 18% | 6519.5 | [7 empty] | ACDB | 1 nos | 18% | 1303.9 |  | ACDB | 1 nos | 1105 | 18% | 1303.9
| Mounting structure (GI) | LS | 105000 | 18% | 123900 | [7 empty] | Mounting structure (GI) | LS | 18% | 21796.5 |  | Mounting structure (GI) | LS | 21000 | 18% | 24780
| Earthing rod | 7 nos | 6720 | 18% | 7929.6 | [7 empty] | Earthing rod | 2 nos | 18% | 1585.92 |  | Earthing rod | 2 nos | 1344 | 18% | 1585.92
| Lightning arrestor | 3 nos | 5880 | 18% | 6938.4 | [7 empty] | Lightning arrestor | 1 nos | 18% | 1387.68 |  | Lightning arrestor | 1 nos | 1176 | 18% | 1387.68
| MC4 connectors | 14 nos | 900 | 18% | 1062 | [7 empty] | MC4 connectors | 3 nos | 18% | 212.4 |  | MC4 connectors | 4 nos | 180 | 18% | 212.4
| Pins & other accessories | LS | 8400 | 18% | 9912 | [7 empty] | Pins & other accessories | LS | 18% | 1982.4 |  | Pins & other accessories | LS | 1680 | 18% | 1982.4
| Design & Installation | LS | 65000 | 18% | 76700 | [7 empty] | Design & Installation | LS | 18% | 15340 |  | Design & Installation | LS | 13000 | 18% | 15340
| TOTAL PRICE (incl. GST) |  |  |  | 550082.27 | [7 empty] | TOTAL PRICE (incl. GST) |  |  | 107032.954 |  | TOTAL PRICE (incl. GST) |  |  |  | 121949.914
| ADDITIONAL COST (to be assessed after site visit) : | [11 empty] | ADDITIONAL COST (to be assessed after site visit) : |  |  |  |  | ADDITIONAL COST (to be assessed after site visit) :
| DC cable | [11 empty] | DC cable |  |  |  |  | DC cable
| Earthing cable | [11 empty] | Earthing cable |  |  |  |  | Earthing cable
| 4sq mm AC cable | [11 empty] | 4sq mm AC cable |  |  |  |  | 4sq mm AC cable
| CUSTOMER SCOPE: | [11 empty] | CUSTOMER SCOPE: |  |  |  |  | CUSTOMER SCOPE:
| Electrical works | [11 empty] | Electrical works |  |  |  |  | Electrical works
| Civil works | [11 empty] | Civil works |  |  |  |  | Civil works
| TANGEDCO fee | [11 empty] | TANGEDCO fee |  |  |  |  | TANGEDCO fee
QUOTATION
MATTERLESS TECHNOLOGIES OPC PRIVATE LIMITED FORGE FACTORY, KCT TECHPARK, 03 ATHIPALAYAM ROAD, COIMBATORE - 641049 GST: 33AATCM6353J1ZZ Ph: 9087610051
| To |  |  |  | 08.04.2026
Avinashi
| Items | Details | Basic Cost | GST % | Final Cost
| Panels (Warree TOPCon) | 700 | 196000 | 5% | 205800 | 16 panels
| Panels (Adani TOPCon) | 625 | 202500 | 5% | 212625 | 18 panels
| Inverter (Deye 1-ph On-Grid) | 10kW (1 ph) | 45281 | 5% | 47545.05
| DCDB | 1 nos | 7750 | 18% | 9145
| ACDB | 1 nos | 4250 | 18% | 5015
| Earthing rod | 3 nos | 2457 | 18% | 2899.26
| Lightning arrestor | 1 nos |  | 18%
| MC4 connectors | 15 nos | 630 |  | 743.4
| Mounting structure | LS |  | 18% | 60k+
| Pins & other accessories | LS
Design / Installation / Logistics
| TOTAL PRICE (incl. GST) |  |  |  | 271147.71
ADDITIONAL COST (to be assessed after site visit) :
| DC cable (Panels to DCDB/Inverter) | 6 sq. mm
| AC cable (Inverter to ACDB) | 6 sq. mm 4-core
| AC cable | 4 sq mm
| Earthing cable | DC (6 sq. mm) | ~66/m
|  | DC (10 sq. mm) | ~139/m
|  | AC (6 sq. mm) | ~100/m
|  | AC (10 sq. mm) | ~150/m
CUSTOMER SCOPE:
Electrical works
Civil works
TANGEDCO fee

## Commercial_sizing
| Months | (2025-2026) kWh | (2025-2026) Bill | Avg Rs. /kWh | (2024-2025) kWh | (2024-2025) Bill | Avg Rs. /kWh 2 | Daily kWh | Column 1 | Min | Max | units | Ratio
Summer | April | [7 empty] | Daily Consumption (AC) | 103.4 | 145.6667 | kWh
Summer | May | 6961 | 66547.16 | 9.56 | 6568 | 59998.68 | 9.135 | 116.0167 | Daytime energy needed (AC) | 82.72 | 116.5333 | kWh | 80%
Rainy | June | [7 empty] | Desired AC output (from inverter) | 15.04 | 21.1879 | kW
Rainy | July | 8740 | 84865.4 | 9.71 | 9710 | 90351.55 | 9.305 | 145.6667 | Power Factor (PF) | 0.9 | 0.9
Dry / windy | August | [7 empty] | Required AC output (from inverter) | 16.7111 | 23.5421 | kVA |  | Reactive power (kVA) (i.e. useful energy) = Desired AC output / PF
Dry / windy | September | 7623 | 75239.01 | 9.87 | 7152 | 68373.12 | 9.56 | 127.05 | Corresponding DC sizing | 20.0533 | 28.2505 | kW |  | DC/AC ratio = 1.25
Rainy | October
Rainy | November | 7037 | 69455.19 | 9.87 | 6345 | 60658.2 | 9.56 | 117.2833 | Panel Wp | 560 | 700
Winter | December | [7 empty] | No of panels | 42 | 42 | -3 | 2
Winter | January | 6223 | 61421.01 | 9.87 | 7949 | 75992.44 | 9.56 | 103.7167 | Available inverter size (kW) | 20 | 25
Summer | February | [7 empty] | Actual DC sizing (kW) | 23.52 | 29.4
Summer | March | 6204 | 61233.48 | 9.87 | 7253 | 69338.68 | 9.56 | 103.4 | Actual DC/AC ratio | 1.176 | 1.176
| TOTAL | 42788 | 418761.25 |  | 44977
| Min = | 6204 | [5 empty] | 103.4 | Estimated BESS kWh | 20.68 | 29.1333
| Max = | 8740 | [5 empty] | 145.6667 | Available BESS kWh | 20 | 20
[9 empty] | DoD | 18 | 18
[9 empty] | Inverter sizing kW | 20 | 25
| Data needed | Column 1
| Average peak sun hour | 5.5 | [6 empty] | Estimated daytime production kWh | 110 | 137.5
| Total system losses (%) | 25
| Derate factor (%) | 0
| Performance ratio | 1
| Months | (2025-2026) kWh | (2025-2026) Bill | Avg Rs. /kWh | (2024-2025) kWh | (2024-2025) Bill | Avg Rs. /kWh 2 | Daily kWh | Column 1 | Min | Max | units | Ratio
Summer | April | [7 empty] | Daily Consumption (AC) | 76.1333 | 86.6 | kWh
Summer | May | 4671 | 49792.86 | 10.66 | 6568 | 59998.68 | 9.135 | 77.85 | Daytime energy needed (AC) | 60.9067 | 69.28 | kWh | 80%
Rainy | June | [7 empty] | Desired AC output (from inverter) | 11.0739 | 12.5964 | kW
Rainy | July | 5196 | 56175.3 | 10.8113 | 9710 | 90351.55 | 9.305 | 86.6 | Power Factor (PF) | 0.9 | 0.9
Dry / windy | August | [7 empty] | Required AC output (from inverter) | 12.3044 | 13.996 | kVA |  | Reactive power (kVA) (i.e. useful energy) = Desired AC output / PF
Dry / windy | September | 4981 | 54654.52 | 10.9726 | 7152 | 68373.12 | 9.56 | 83.0167 | Corresponding DC sizing | 14.7653 | 16.7952 | kW |  | DC/AC ratio = 1.25
Rainy | October
Rainy | November | 4697 | 51538.3 | 10.9726 | 6345 | 60658.2 | 9.56 | 78.2833 | Panel Wp | 700 | 560
Winter | December | [7 empty] | No of panels | 20 | 30 |  | 0 | 38
Winter | January | 4811 | 52789.18 | 10.9726 | 7949 | 75992.44 | 9.56 | 80.1833 | Available inverter size (kW) | 12 | 15 |  |  | 18
Summer | February | [7 empty] | Actual DC sizing (kW) | 14 | 16.8 |  |  | 21.28
Summer | March | 4568 | 50122.84 | 10.9726 | 7253 | 69338.68 | 9.56 | 76.1333 | Actual DC/AC ratio | 1.1667 | 1.12 |  |  | 1.1822
| TOTAL | 28924 | 315073 |  | 44977
| Min = | 4568 | [5 empty] | 76.1333 | Estimated BESS kWh | 15.2267 | 17.32
| Max = | 5196 | [5 empty] | 86.6 | Available BESS kWh | 20 | 20
[9 empty] | DoD | 18 | 18
[9 empty] | Inverter sizing kW | 12 | 25
| Data needed | Column 1
| Average peak sun hour | 5.5 | [6 empty] | Estimated daytime production kWh | 66 | 82.5
| Total system losses (%) | 25
| Derate factor (%) | 0
| Performance ratio | 1

## Hybrid system sizing calculator
1. Analyse energy consumption for 1-2 years --> calculate per day load consumption --> Calculate solar panel & inverter sizing
2. Identify possible types of heavy loads (eg. EV vehicles, ACs, Geysers, etc.)
3. Identify loads that need backup (for comfort and partial independence from grid)
4. Calculate backup hours --> calculate BESS capacity
Months | 2025-2026 | 2024-2025 |  | Column 1 | Normal System | EV alone | units
April | 749.11 | 1051 |  | Daily Consumption (AC) | 100 | 21.0857 | kWh
June | 705.4 | 1239 |  | Energy Needed (AC) | 100 | 21.0857 | kWh
August | 405.58 | 421 |  | Desired AC output (from inverter) | 18.1818 | 3.8338 | kW
October | 415.02 | 536 |  | Power Factor (PF) | 0.8 | 0.99
December | 399 | 521 |  | Required AC output (from inverter) | 22.7273 | 3.8725 | kVA |  | Reactive power (kVA) (i.e. useful energy) = Desired AC output / PF
February | 416.2 | 432 |  | Corresponding DC sizing | 28.4091 | 4.8406 | kW |  | DC/AC ratio = 1.1. to 1.25
| 3090.31 | 4200
Daily consumption (kWh) = | 8.4666 | 11.5068
Data needed | Column 1 |  |  | Parameters | Units | Details
Average peak sun hour | 5.5 |  |  |  | kWh
Total system losses (%) | 25
Derate factor (%) | 0
Performance ratio | 1
Months | Energy usage (units) | Column 1
EV Brand name | TATA Nexon | MG ZS
Battery Capacity | 30 | 45 |  | Panels Age(Years) | Expected Output N.S (KWh) | Expected Output with EV (KWh)
Full charging times per week | 3 | 4 |  | 10 | 17.2929 | 3.6463
Half charging times per week | 4 | 3 |  | 15 | 16.8649 | 3.5561
Extra power needed(KWh) per day | 19.2857 | 31.8214 |  | 20 | 16.4475 | 3.4681
[5 empty] | w/o EV | with EV
Months | Energy usage (units) |  |  | Panel Wp | 620 | 615
EV Brand name |  |  |  | No of panels | 46 | 54
Battery Capacity | 3.5 |  |  | Actual DC sizing (kW) | 28.52 | 33.21
Full charging times per week | 4 |  |  | Actual DC/AC ratio | 1.2549 | 1.2485
Half charging times per week | 3 |  |  | Available inverter size (kW) | 3 | 6
Extra power needed(KWh) per day | 1.8 |  |  | Final no of panels | 4 | 54
|  |  |  | Final system size (kW) | 2.48 | 33.21
|  |  |  | Hours |  | Load kWh |  |  |  | BESS kWh
| Loads |  |  | MIN | MAX | MIN | MAX | Total kWh consumption |  | MIN | MAX
All months | Critical |  |  |  |  | 10 | 15 | 15 | into consideration | 12.3457 | 18.5185 | (Lighting, Fan, Fridge, Security cameras, Gate automation, ... )
Summer months | HVAC | Low solar hours | Morning (6am to 10am) | 2 | 4 | 40 | 80 |  | not into consideration | 49.3827 | 98.7654
| HVAC | High solar hours | Late morning/afternoon (10am to 5pm) | 4 | 7 | 80 | 140 |  | not into consideration | 98.7654 | 172.8395
| HVAC | Non-solar hours | Evening/night (5pm to 6am) | 6 | 13 | 120 | 260 | 180 | into consideration | 148.1481 | 320.9877
Non-summer months | HVAC | Low solar hours | Morning (6am to 10am) | 0 | 1 | 0 | 20 |  | not into consideration | 0 | 24.6914
| HVAC | High solar hours | Late morning/afternoon (10am to 5pm) | 0 | 2 | 0 | 40 |  | not into consideration | 0 | 49.3827
| HVAC | Non-solar hours | Evening/night (5pm to 6am) | 2 | 6 | 40 | 120 | 80 | into consideration | 49.3827 | 148.1481
All months | EV |  | Evening/night (8pm to 8am) | 6 | 12 | 25.5536 | 51.1071 | 51.1071 | into consideration | 31.5476 | 63.0952
HVAC capacity (kW) = | 20
Amps (A) = | 30
DoD = | 90%
Inverter/battery efficiency = | 90%
Required BESS (kWh) in Summer = | 200 | Primarily, to offset HVAC load at night (8 hours)
Required BESS (kWh) in non-Summer = | 50 | Primarily, to offset HVAC load at night (upto 2 hours)
Required solar kW = | 36.3636

## DCDB & ACDB
Parameters | Values | Units | Parameters | Values | Units
System capacity | 5 | KW | System capacity | 4 | KW
DC input voltage | 400 | V | AC supply voltage | 415 | V
|  |  | Phase | 3 | ø
Saftey Factor | 30%
|  |  | AC fuse rating | 7.2343 | A
DC fuse rating | 16.25 | A
(System Size /SQRT(phase) * AC Input V * power factor )*(Safety factor )
SPD RATING
More than 600V in string | 1000V
Less than 600V in string | 600V

## Battery sizing
Appliances | NOs | power(W) | Total power | No of hours | energy (Wh)
Lights | 5 | 10 | 50 | 6 | 300
Fan | 4 | 70 | 280 | 6 | 1680 |  | daily consumption x day of atonomy /D.O.D x System voltage
TV | 1 | 150 | 150 | 2 | 300
AC | 2 | 1500 | 3000 | 2 | 6000
Chargers | 3 | 10 | 30 | 2 | 60
Refrigerator | 1 | 150 | 150 | 3 | 450
Computers | 1 | 250 | 250 | 6 | 1500
Others | 1 | 300 | 300 | 2 | 600
Total |  |  | 4210 |  | 10890
Mode | Energy used (WH) | Bateery needed (Kwh) | battery V | Battery AH | Total capacity | Column 1 | Run time | Run Time(h) (3.3KWH) | Run Time(h) (4.1KWH) | Run Time(h) (8KWH)
Basic - Lights & Fans | 1980 | 3.2175 | 24 | 134.0625 | 3.2175 |  | 9.75 | 9.75 | 12.2614 | 53.625
Semi Advanced - Lights , Fans , Refrigerator,charges | 2490 | 4.0462 | 24 | 168.5938 | 4.0462 |  | 7.9338 | 6.3088 | 7.9338 | 34.6985
Advanced - All | 10890 | 17.6962 | 48 | 368.6719 | 17.6962 |  | 4.2034 | 0.76425 | 0.9611 | 4.2034

## Wiring
Practical DC WIRING SIZING
Panels Specs | Values(V&I)
Vmp | 23 |  | CURRENT/DISTANCE | 10m | 25m | 50m | 100m | Indian Standards for DC Cables: • Minimum DC cable size: 4mm² • Voltage drop limit: 2% for DC circuits • Material: XLPE or XLPO insulated copper cables • Standards: IS 7098 Part I & II
Imp | 12 |  | 10A | 2.5 | 4 | 6 | 16
|  |  | 20A | 4 | 6 | 16 | 25
|  |  | 30A | 6 | 10 | 25 | 35
|  |  | 40A | 10 | 16 | 35 | 50
No of panels in a string | 4 |  | 50A | 16 | 25 | 50 | 70
No of Strings | 2
Safety factor | 1.25
Practical AC WIRING SIZING
|  |  | CURRENT/DISTANCE | 10m | 25m | 50m | 100m | Indian Standards for AC Cables: • Minimum AC cable size: 4mm² • Voltage drop limit: 2% from inverter to distribution board • Material: PVC or XLPE insulated copper cables • Neutral wire: Same size as phase wires in 3-phase systems
Copper quick ref (20 °C, Ω/m): 2.5 mm²: 0.00741 4 mm²: 0.00461 6 mm²: 0.00308 10 mm²: 0.00183 16 mm²: 0.00115 |  |  | 16A | 2.5 | 2.5 | 4 | 6
|  |  | 25A | 2.5 | 4 | 6 | 10
|  |  | 32A | 4 | 6 | 10 | 16
|  |  | 40A | 6 | 10 | 16 | 25
|  |  | 63A | 10 | 16 | 25 | 35
DC Wire Sizing | Values 1 | Units
Isc | 11 | A
safety Factor And Contionous Load | 1.56 | %
Current | 17.16 | A
Length | 10 | L
Panel Voltage Vmmp | 42.5 | V
No of Pnaels | 8
System Voltage | 340 | V
Voltage Drop | 1.5822 | V
Recomonded less than 2 % | 0.46534 | %
AC Wire Sizing | Values 2 | Units
Output Power | 5000 | W
Voltage | 230 | A
Efficiency | 0.97 | %
Power Factor | 0.9 | A
Current | 18.9783 | A
Length | 10 | L
Voltage Drop | 1.7498 | V
Recomonded less than 2 % | 0.76078 | %
Voltage Drop 3 phase | 1.5154

## Missmatch loss
Parameter | Reliance HJT 700Wp | Renewsys TOPCon (585Wp) | units | Difference
Pmax | 700 | 585 | Wp | HJT +20% power
Vmpp | 41.5 | 42.87 | V | 3.3% (TOPCon higher V)
Impp | 16.8675 | 13.6459 | A | HJT +23.6% current
Voc | 49.5 | 52.3 | V | 5.7% (TOPCon higher)
Isc | 17.8 | 13.75 | A | HJT +29.5% short-circuit
String | Voltage (6xVmpp) | Current (Impp) | Power Output(Kw)
HJT | 249 | 16.86 | 4.1981
TOPCon | 257 | 13.64 | 3.5055
Theoretical Total |  |  | 7.7036
BEFORE Mismatch: 7.7 kW total AFTER Clipping: HJT clipped to 13.64A - 249V × 13.64A = 3.4 kW (loss 19.1%) TOPCon unchanged: 3.5 kW NEW TOTAL: 6.9 kW Mismatch Loss: 10.4% (800W lost)

## Enphase
System size = | 8000
Inverter system | Item |  | Unit price | Qty | Total Price | GST | Final Price
On-grid | Microinverter | IQ8P-72-2-INT | 7900 | 16.8421 | 133052.6316 | 5% | 139705.2632
| Cables | Q-12-10-240 | 550 | 16.8421 | 9263.1579 | 5% | 9726.3158
| Accessories | IQ-TERM-10 | 690 | 3 | 2070 | 5% | 2173.5
|  | IQ-DISC-10 | 200 | 1 | 200 | 5% | 210
| Gateway | ENV-S-WM-230 | 12400 | 1 | 12400 | 5% | 13020
| IQ Relay 3P |  | 5150 | 1 | 5150 | 5% | 5407.5
| CT | 200A | 1450 | 4 | 5800 | 5% | 6090
[7 empty] | 1.7633 | Lakhs
Hybrid | Comm cable | I-ENPHASE-CTRL-BL-EU-01 | 500 | 5 | 2500 | 18% | 2950
| System Controller | I-SC100G-M230INT | 107000 | 1 | 107000 | 18% | 126260
| 5kWh 3P BESS | I-IQBATTERY-5P-3P-INT | 290000 | 1 | 290000 | 18% | 342200
[7 empty] | 4.7141 | Lakhs
BIG MINUS:
i) 17 panels vs 12 panels with 8kW string inverter system (due to smaller rated output power at 475W)
ii) Total inverter system cost is 4x (with Deye on-grid) or 2x (with Deye hybrid)